## CS Selector
|  | Size | Fig No 4017 | MS signal (kPa) | Total pressure drop @ 100% open | Velocity (m/s) | Fig No | Size | Kvs Value | Kv max value | Medium Gr | Area | Velocity | Selection Guidelines
|  | DN15 LF | 1401711 | 0 | 0 |  | 4017-11 | 1/2" LF | 0.48 | 0.46 | 16.2 | 0.20615 | 0 | DP Signal
|  | DN15 MF | 1401721 | 0 | 0 |  | 4017-12 | 1/2" MF | 0.97 | 0.88 | 16.2 | 0.20615 | 0 | Commissioning valves should be selected with a minimum signal of 1 kPa in accordance with CIBSE Code W: 2010 and BSRIA Guide BG 2/2010 Commissioning Water Systems.
|  | DN15 | 1401701 | 0 | 0 |  | 4017-01 | 1/2" | 1.95 | 2 | 16.2 | 0.20615 | 0
|  | DN20 | 1401702 | 0 | 0 |  | 4017-02 | 3/4" | 3.95 | 3.6 | 21.7 | 0.36988 | 0
|  | DN25 | 1401703 | 0 | 0 |  | 4017-03 | 1" | 7.9 | 6.5 | 27.4 | 0.58972 | 0 | The maximum DP signal which can be read with a flurocarbon manometer is 4.7 kPa, higher signals can be read with mercury or digital manometers
Flowrate | l/s | DN32 | 1401704 | 0 | 0 |  | 4017-04 | 1 1/4" | 15.75 | 13.3 | 36.1 | 1.0237 | 0
|  | DN40 | 1401705 | 0 | 0 |  | 4017-05 | 1 1/2" | 21.5 | 18.5 | 42 | 1.3856 | 0
|  | DN50 | 1401706 | 0 | 0 |  | 4017-06 | 2" | 46.7 | 33 | 53.1 | 2.2148 | 0 | Velocity
|  | DN65 | 1421881CS | 0 | 0 |  | 4218-71CS | 65 | 100.7 | 62.34 | 68.8 | 3.7181 | 0 | Maximum flow velocities according to CIBSE Guide C and BSRIA Guide BG 2 / 2010 are as follows:-
|  | DN80 | 1421882CS | 0 | 0 |  | 4218-72CS | 80 | 133.8 | 96.74 | 80.8 | 5.1282 | 0
|  | DN100 | 1421883CS | 0 | 0 |  | 4218-73CS | 100 | 237.7 | 155.78 | 105.1 | 8.6766 | 0 | Sizes DN15 - DN50 = 1.15 m/s (CIBSE)
|  | DN125 | 1421884CS | 0 | 0 |  | 4218-74CS | 125 | 339 | 233.73 | 129.65 | 13.2036 | 0 | Sizes DN15 - DN50 = 1.5 m/s (BSRIA steel pipe)
|  | DN150 | 1421885CS | 0 | 0 |  | 4218-75CS | 150 | 511 | 355.45 | 155.1 | 18.896 | 0 | Sizes DN65 - DN300 = 3 m/s
|  | DN200 | 1421886CS | 0 | 0 |  | 4218-76CS | 200 | 858 | 612.71 | 206.5 | 33.4955 | 0
|  | DN250 | 1421887CS | 0 | 0 |  | 4218-77CS | 250 | 1235 | 961.33 | 260.4 | 53.2633 | 0
|  | DN300 | 1421888CS | 0 | 0 |  | 4218-78CS | 300 | 1793 | 1538.05 | 309.7 | 75.3405 | 0